ITC-22431-X-R – Specifications

CONTROL PANEL:

Where shown on Drawings, provide an ISIMET – ITC Series Control Panel, Model

ITC-32431.  Panel shall be Brushed Stainless Steel with Gray Powder Coat concealed wall box provided with panel service switch, low voltage transformer and output terminal. Panel shall comply with UL508-A, Standards for Industrial Control Panels.

Panel shall have Twenty Four Hour programmable timer and an integral printed circuit board with logic device to provide a 24-vac output circuit to activate utilities as shown on drawings. Activation of output circuit shall be automatic and preset for one minute, but adjustable up to five minutes.

Front panel shall be Stainless Steel with Off On switch and green indicator to show when unit is on.  Panel shall have keyed switch to allow for OFF, automatic usage and manual override for flushing at other time periods.  Panel shall contain an incandescent amber indicator which shall illuminate when solenoid is active.

Provide connection point with reset switch for connection to the solenoid.

SOLENOIDS:

Furnish Series 220 lead free solenoid with Y-strainer for water system.  Solenoid coil shall be 24-vac.  Solenoid coil shall be UL listed. Thoroughly flush piping system prior to placing into service.  Size of solenoid shall be as indicated on the drawings.