LA Series Utility Controller – Specifications

CONTROL PANEL:

At each science classroom and elsewhere as shown on Drawings, provide an ISIMET - LA Series Control Panel Model 1213 Dual 24-vac output.  Panel shall be brushed stainless steel with concealed wall box provided with panel service switch, low voltage transformer and fuse block.  Wall box shall be NEMA 1 rated.  Panel shall comply with UL508-A, Standards for Industrial Control Panels.

Panel shall have integral printed circuit board with logic device to provide 24-vac output circuits to activate utilities as shown on drawings.  Number of output circuits as noted on drawings.  Activation of output circuits shall be enabled only by switch ON and then keying.

The Panel shall be equipped with a service switch for each output circuit and a momentary enabling key switch.  Deactivation of output circuits shall not require engagement of enabling key.  Panel shall be provided with N/O momentary panic button assembly to deactivate output circuits in case of emergency.  Reset after panic shall occur by re-keying.

Provide panel with additional terminals for integration of ISIMET Remote Panic Button Assembly, and opto-isolated input terminal for integration with facility’s alarm system.  A fire alarm signal shall deactivate all utilities controlled by the LA Series Control Panel.

Provide panel with dry contact terminals for output integration.  ISIMET “Panic” shall provide a notification signal to a secondary alarm monitoring system.  Reset of Controller shall withdraw notification signal.

SOLENOIDS:

Furnish and install ISIMET Series 200 normally closed general service, 2 psi differential solenoids at each domestic water utility service.  Furnish Series 300 for all natural gas systems.   Solenoid coil shall be 24-vac.  Provide a ball valve up-stream from solenoid and wye-strainer on all fluid delivery systems.  Thoroughly flush piping system prior to placing into service.  Final connection to coil from Control Panel by electrical contractor.  Solenoids shall close upon loss of operating power and require re-keying for reactivation of service.  Provide solenoids in ISIMET S-Series Enclosure, Model # S-1212-1-X-X-K-F-R-U.  Solenoid sized as shown on drawings.

ELECTRIC CONTACTS:

Where electric service is controlled by the system, provide ISIMET E-Series Enclosure, Model # E-31X-S-L.  Number of contacts and location as shown on drawings.

WIRING:

Do not install wiring or cable for integrated systems, remote panic assemblies or other interface wiring within conduit for either 24-vac control or 120-vac line voltage.  Each wiring system should be housed in independent conduit and not bundled with wiring for other systems.