LSP – Laboratory Service Panel – Domestic Water System – Specifications

CONTROL PANEL:

At each science classroom and elsewhere as shown on Drawings, provide an ISIMET – LSP – Laboratory Service Panel.  Panel shall have brushed stainless steel door panel and trim with gray powder coated enclosure provided with low voltage transformer and fuse block.  Enclosure shall be NEMA 1 rated. Panel shall be labeled “DOMESTIC WATER SERVICE PANEL”.  Panel shall comply with UL508-A, Standards for Industrial Control Panels.

Panel shall have integral printed circuit board with logic device to provide 24-vac output circuit to activate integral 24-vac general service solenoid.  Activation of output circuit shall be enabled only by switch ON and then keying.

The Panel shall be equipped with a service switch and a momentary enabling key switch.  Deactivation of output circuit shall not require engagement of enabling key.  Panel shall be provided with N/O momentary panic button assembly to deactivate output circuit in case of emergency.  Reset after panic shall occur by re-keying.  Green LED shall indicate operation ON.  Red LED shall indicate that shut-down has occurred due to pressing the panic button.

Provide panel with additional terminals for integration of ISIMET Remote Panic Button Assembly and opto-isolated input terminal for integration with facility’s alarm system.  A fire alarm signal shall deactivate the utility controlled by the LSP Series Panel.

Provide panel with dry contacts terminals for output integration.  ISIMET “Panic” shall provide a notification signal to a secondary alarm monitoring system.  Reset of Service Panel shall withdraw notification signal.

Line and 24-vac control wiring furnished and installed by electrical contractor.

SOLENOID:

Service Panel shall be furnished with ISIMET Series 200 normally closed general service 2 psi differential solenoid.  Solenoid coil shall be 24-vac.  Service Panel shall be provided with a ball valve.  Furnish and install a wye strainer directly up-stream from solenoid assembly.  Thoroughly flush piping system prior to placing into service.

PIPING SYSTEMS CONFIGURATIONS:

Where hot and/or cold water is indicated by drawings to be routed to an emergency eyewash and/or emergency drench shower, this piping should be connected to piping systems prior to isolation solenoid valves operated by the ISIMET control unit.